## Slide 1
PMT Eric Weng
Dec,2016
Servo | AC Drive | PLC | Motor | Robotic | IOT | Renewable Energy
H3U
Forward, Always Progressing!
Version 1.0
PartⅡ
Technology
High Performance Small PLC

## Slide 2
Installation Practice
CONTENTS
Wiring Specifications
PART 2
PART 1
PART 3
Getting Started
Technical
PART 4
Diagnostics

## Slide 3
1. Installation Practice
1.1 Installation Environment
1.2 Mounting Orientation and Clearance
1.3 Installation Method and Procedures
1.4 Recommended External Components

## Slide 4
Installation Practice
PART 1
1.1 Installation Environment
Item | Specifications |  |  |  | 
Ambient temperature | Running: -5~55C, storage: -25~75C |  |  |  | 
Relative humidity | Running: 5~95%RH (non-condensing) |  |  |  | 
Vibration |  | Frequency (Hz) | Acceleration (m/s2) | One-way amplitude (mm) | Ten times in each of the X, Y and Z direction for 80 minutes
 | When DIN rail is installed | 10~57 | -- | 0.035 | 
 |  | 57~150 | 4.9 | -- | 
 | When PLC is directly installed | 10~57 | -- | -- | 
 |  | 57~150 | 9.8 | 0.075 | 
Working environment | Do not use the PLC in environments with strong erosive and flammable gases or conductive dust. |  |  |  | 
Elevation | Below 2000 m |  |  |  | 

## Slide 5
1.2 Mounting Orientation and Clearance
Installation Practice
PART 1
Vertical upward installation

## Slide 6
1.2 Mounting Orientation and Clearance
Installation Practice
PART 1
To ensure properly ventilation, the distance A between the PLC and modules should be larger than 50 mm.

## Slide 7
1.3 Installation Method and Procedures
Installation Practice
PART 1
Backplate Mounting
Use M4 screws to fix the PLC on the installation surface in the control cabinet through the mounting holes on four corners

## Slide 8
1.3 Installation Method and Procedures
Installation Practice
PART 1
DIN Rail Mounting
1.Clip the mounting slot on the rear side of the PLC in the upper edge of the rail.
2. Press the PLC in the direction B until you hear the click sound. Check if the PLC is fully and vertically clipped in on the DIN rail.

## Slide 9
1.3 Installation Method and Procedures
Installation Practice
PART 1
DIN Rail Mounting
1.Clip the mounting slot on the rear side of the PLC in the upper edge of the rail.
2. Press the PLC in the direction B until you hear the click sound. Check if the PLC is fully and vertically clipped in on the DIN rail.

## Slide 10
1.3 Installation Method and Procedures
Installation Practice
PART 1
Expansion Modules Installation
Unlock
Lock

## Slide 11
Installation Practice
CONTENTS
Wiring Specifications
PART 2
PART 1
PART 3
Getting Started
Technical
PART 4
Diagnostics

## Slide 12
2. Wiring Specifications
2.1 Terminals
2.2 Input Wiring
2.3 Output Wiring
2.4 Communication Instructions

## Slide 13
2.1 Terminals
PART 2
Wiring Specifications

## Slide 14
2.1 Terminals
PART 2
Wiring Specifications

## Slide 15
2.1 Terminals
PART 2
Wiring Specifications

## Slide 16
2.2 Input Wiring
PART 2
Wiring Specifications
Normal input wiring
Leaking type
Source type

## Slide 17
2.2 Input Wiring
PART 2
Wiring Specifications
High-speed input wiring
Leaking type
Source type

## Slide 18
2.2 Input Wiring
PART 2
Wiring Specifications
Differential input wiring
Leaking type
Source type
Standard method

## Slide 19
2.3 Output Wiring
PART 2
Wiring Specifications
Normal/high-speed transistor output wiring

## Slide 20
2.3 Output Wiring
PART 2
Wiring Specifications

## Slide 21
2.3 Output Wiring
PART 2
Wiring Specifications
Wiring of relay outputs

## Slide 22
2.3 Output Wiring
PART 2
Wiring Specifications

## Slide 23
2.3 Output Wiring
PART 2
Wiring Specifications
Wiring of High-speed differential outputs

## Slide 24
2.3 Output Wiring
PART 2
Wiring Specifications
CLR outputs of H3U-0808PMRTA

## Slide 25
2.4 Communication Instructions
PART 2
Wiring Specifications
Functions of communication terminals
Name | Description | 
+24V,CGND | CAN communication power supply, setting range is between 9-30 V | 
CANL,CANH | CAN communication cable, the reference level is CGND. CGNDs must be connected to each other when there are multiple stations. | 
 | It is the shield layer, which should be connected according to the actual need. | 
485+, 485- | It is used to connect the RS485 communication signal cable. | 
GND | It is for the reference signal of the RS485 communication signal. | 

## Slide 26
PART 2
Wiring Specifications
2.4 Communication Instructions
Communication configuration of H3U-3232MT/R and H3U-0808PMRTA

## Slide 27
PART 2
Wiring Specifications
Communication configuration of
H3U-1616MT/R-XP
2.4 Communication Instructions

## Slide 28
Installation Practice
CONTENTS
Wiring Specifications
PART 2
PART 1
PART 3
Getting Started
Technical
PART 4
Diagnostics

## Slide 29
3. Getting Started
3.1 Tools Requirements
3.2 Hardware Connection
3.3 Installation of AutoShop
3.4 Program Download Procedure

## Slide 30
Part Code：15041200
Getting Started
PART 3
3.1 Tools Requirements
USB2.0 to Laptop
mini USB to PLC

## Slide 31
Getting Started
PART 3
3.2 Hardware Connection

## Slide 32
Getting Started
PART 3
3.3 Installation of AutoShop
Step 1: Double click the(the present version is V2.62 for English.)
Step 2: Click “Next” and “Next” .

## Slide 33
Getting Started
PART 3
Step 4: Wait until the installation complete, click “Close”. Finished
Step 3: Click “Install”.
3.3 Installation of AutoShop

## Slide 34
Getting Started
PART 3
3.4 Program Download Procedure
Step 1:
1.Power on PLC
2.Double click the “AutoShop”
3.Click “File” and select “New Project”

## Slide 35
Getting Started
PART 3
3.4 Program Download Procedure
Step 2: Set as follows figure.

## Slide 36
Getting Started
PART 3
3.4 Program Download Procedure
Step 3:Click “Tools” and select “Communication Setting” .

## Slide 37
Getting Started
PART 3
3.4 Program Download Procedure
Step 4: Follow below steps1-2-3-4.

## Slide 38
Getting Started
PART 3
3.4 Program Download Procedure
Step 5: When you finish coding, follow below step to download program.

## Slide 39
Getting Started
PART 3
3.4 Program Download Procedure
Step 5: When you finish coding, follow below step to download program.

## Slide 40
Getting Started
PART 3
3.4 Program Download Procedure
Step 6:The output window indicates the download executed .

## Slide 41
Getting Started
PART 3
3.4 Program Download Procedure
Step 9:
1.Switch to the “RUN”.
2.The RUN light is ON.

## Slide 42
Getting Started
3.4 Program Download Procedure
Step 10:
1.Click “monitor” widget to start monitoring program.
2.The lamps of PLC Status and Fault turn green.
PART 3

## Slide 43
Installation Practice
CONTENTS
Wiring Specifications
PART 2
PART 1
PART 3
Getting Started
Technical
PART 4
Diagnostics

## Slide 44
4. Diagnostics
4.1 Common Faults Expressed by Fault Codes

## Slide 45
4.1 Common Faults Expressed by Fault Codes
Diagnostics
PART 4
Error Code | Content
D8060 | I/O range or setting error
1000-1377 | X input signal error, serial number error or exceeding limit
0000-0377 | Y input signal error, serial number error or exceeding limit

## Slide 46
Diagnostics
PART 4
Error Code | Content
D8061 | PC hardware error definition
6101 | RAM error
6102 | Operation loop error
6103 | I/O hardware connection error
6104 | External 24V power error
6105 | System monitor error
6106 | System flash read/write error
6107 | System I/O setting error
6108 | FPGA download error
6109 | FPGA configuration data error in flash
6110 | Ethernet hardware initialization failure
6111 | Extension module configuration different from the actual
6112-6199 | Reserved
16100-16199 | Reserved
26100-26199 | Reserved
4.1 Common Faults Expressed by Fault Codes

## Slide 47
Diagnostics
PART 4
Error Code | Content
D8062 | Communication error in control panel or program connection port
6200-6279 serial communication and configuration error codes | 
6201 | Receiving timeout
6202 | CAN transmitting busy
6203 | CAN receiving busy
6204 | Data format incorrect
6205 | Instruction incorrect
6206 | Communication element exceeding range
6207 | Communication port exceeding range or not existing
6208-6279 | Reserved
6280-6299 | CAN communication configuration error code
16200-16219 Ethernet configuration error code | 
16200 | Reserved
16201 | Ethernet configuration: function codes not supported
16202 | Ethernet configuration: register start address incorrect or start address plus number of registers incorrect
16203 | Ethernet configuration: number of registers too large
16204 | Ethernet configuration: reading/writing register failed.
16205 | Ethernet configuration: ACK signal
16206 | Ethernet configuration: slave busy
16207 | Ethernet configuration: station number incorrect
16208 | Ethernet configuration: memory check error
16209 | Reserved
16210 | Ethernet configuration: gateway path error
16211 | Ethernet configuration: destination gateway path error
16212-16215 | Reserved
16216 | Ethernet configuration: IP address illegal
16217-16219 | Reserved
16220-16239 | Extension module configuration error code
16240-16259 | USB communication configuration error code
16260-16279 motion control configuration error code | 

## Slide 48
Diagnostics
PART 4
4.1 Common Faults Expressed by Fault Codes
Error Code | Content
D8062 | Communication error in control panel or program connection port
16260 | Mechanical unit setting value incorrect
16261 | Electronic gear ratio setting value incorrect
16262 | Cam table not configured in software being used
16263 | No external input master axis selected for electronic cam
16264 | Electronic cam slave axis speed exceeding maximum output speed allowed
16265 | Synchronization lower limit larger than upper limit
16266 | Master axis setting exceeding range
16267 | Delayed startup pulses setting incorrect
16268 | Instruction written in cam key point, value of key point illegal
16269 | Cam encrypted, not allowing instruction to read key point data
16270 | Electronic cam slave axis zooming incorrect
16271 | Electronic cam configuration unit incorrect
16272 | Failure in modifying electronic cam during running
16273 | Electronic cam modification instruction used repeatedly
16274-16279 | Reserved
16280-16299 | Reserved
26200-26299 | Reserved

## Slide 49
Diagnostics
PART 4
4.1 Common Faults Expressed by Fault Codes
Error Code | Content
D8063 | Communication error
6300-6379 COM0 to COMx serial communication error code | 
6301 | Odd/Even check error, overflow error, frame error
6302 | Communication character incorrect
6303 | Communication data sum inconsistent
6304 | Data format incorrect
6305 | Instruction incorrect
6306 | Monitor timer timeout
6307 | Reserved
6308 | Reserved
6309 | Reserved
6310 | Reserved
6311 | Reserved
6312 | Parallel control (1:1) protocol character incorrect
6313 | Parallel control (1:1) protocol sum incorrect
6314 | Parallel control (1:1) protocol format incorrect
6315 | Parallel control (1:1) protocol communication timeout
6316-6329 | Reserved

## Slide 50
Diagnostics
PART 4
4.1 Common Faults Expressed by Fault Codes
Error Code | Content
D8063 | Communication error
6330+10*X | Modbus slave address setting incorrect, address larger than 247
6331+10*X | Data frame length incorrect, returned frame length not meeting requirement, or smaller than 5
6332+10*X | Address incorrect, standard error frame; transmit/receive addresses inconsistent
6333+10*X | CRC check error
6334+10*X | Instruction code not supported, standard error frame; transmit/receive instructions inconsistent; instruction not supported
6335+10*X | Receiving timeout
6336+10*X | Data error, standard error frame
6337+10*X | Reserved
6338+10*X | Frame error, standard error frame
6339+10*X | Serial protocol error, not configuring corresponding protocol when using Modbus or RS instruction

## Slide 51
Diagnostics
PART 4
4.1 Common Faults Expressed by Fault Codes
Error Code | Content
D8063 | Communication error
6380– 6399: CAN communication error code | 
6380 | Transmitting timeout
6381 | Receiving timeout
6382 | CAN transmitting busy
6383 | CAN receiving busy
6384-6399 | Reserved
16300-16319 Ethernet communication error code | 
16300-16311 | Reserved
16312 | Protocol designator error Modbus protocol
16313 | Frame length error
16314 | Frame timeout error
16315 | Frame not recognized by slave (only for master)
16316 | IP address illegal
16317-16319 | Reserved
16320-16339 | Extension module communication error code
16340-16359 | USB communication error code
16360-16379 | Control panel and interface communication error code
16380-16399 | Reserved
26300-26399 | Reserved

## Slide 52
Diagnostics
PART 4
4.1 Common Faults Expressed by Fault Codes
Error Code | Content
D8064 | System parameter setting incorrect
6401 | Program and parameter inconsistent
6402 | Program capacity setting incorrect
6403 | Changeable power failure retentive area of soft element setting incorrect
6404 | Parameter area setting incorrect
6405 | Program area setting incorrect
6406-6424 | Reserved
6425 | User program check error, download data incorrect
6426 | User program, including motion control subroutine program, incomplete
6427 | PLC designator and user program designator not matching
6428 | Factory commissioning error
6429-6452 | Reserved
6453-6465 | Changeable power failure retentive area of soft element setting incorrect
6466-6499 | Reserved
16400-16499 | Reserved
26400-26499 | Reserved

## Slide 53
Diagnostics
PART 4
4.1 Common Faults Expressed by Fault Codes
Error Code | Content
D8065 | User program grammar error
6501 | Reserved
6502 | Reserved
6503 | Instruction parameter error
6504 | Label definition repeated
6505 | Reserved
6506 | Non-defined instruction used
6507 | Label P definition incorrect
6508 | Label I definition incorrect
6509 | Reserved
6510 | Reserved
6511 | High-speed counter and interrupter using same input
6512-6599 | Reserved
16500-16599 | Reserved
26500-26599 | Reserved

## Slide 54
Diagnostics
PART 4
Error Code | Content
D8066 | User program logic loop error
6601-6604 | Reserved
6605 | Incorrect instruction used in STL
6606 | Incorrect instruction in incorrect position
6607 | FOR-NEXT operation error
6608 | MC-MCR operation error
6609-6617 | Reserved
6618 | Instructions allowed only in main program exist in other areas
6619 | Instructions cannot be used in FOR_NEXT
6620 | Nesting level in FOR_NEXT exceeded
6621 | FOR_NEXT quantitative relationship incorrect
6622 | No NEXT instruction
6623 | No MC instruction
6624 | No MCR instruction
6625 | STL used for above consecutive nine times
6626 | Certain instructions cannot be used in STL-RET
6627 | No RET instruction
6628 | Instructions useless in main program
6629 | No P or I
6630 | No SRET or IRET instruction
6631 | SRET cannot be used in the position
6632 | FEND cannot be used in the position
6633-6699 | Reserved
16600-16699 | Reserved
26600-26699 | Reserved

## Slide 55
Diagnostics
PART 4
Error Code | Content
D8067 | Instruction parameter & running parameter incorrect
6701 | CALL&CJ invoking error
6702 | CALL running times larger than 6
6703 | Reserved
6704 | Communication parameter area setting incorrect
6705 | Element not existing or exceeding range
6706 | Data incorrect or exceeding range
6707 | FOR&NEXT, MC, MCR, STL, subroutine program, interruption program relationship not clear
6708 | FROM or TO instruction incorrect
6709 | IRET, SRET, FOR~NEXT relationship not in a match
6710 | Local variable used in main program
6711 | Soft element using in instruction repeated or conflict
6712 | Non-defined interrupt used in system
6713-6719 | Reserved
6720 | CALL instruction SRET not in a match
6721 | Parameter incorrect in subroutine program with parameters
6722 | Manipulator instruction port function conflict
6723-6729 | Reserved
6730 | Sampling time TS < 0
6731 | Reserved
6732 | Input filter constant object abnormal

## Slide 56
Diagnostics
PART 4
Error Code | Content
D8067 | Instruction parameter & running parameter incorrect
6733 | Input proportional coefficient abnormal
6734 | Integral time abnormal
6735 | Differential gain abnormal
6736 | Differential time abnormal
6737 | Reserved
6738 | Reserved
6739 | Reserved
6740 | Sampling time abnormal
6741 | Reserved
6742 | Measured variable overflow
6743 | Offset abnormal
6744 | Integral term abnormal
6745 | Differential value overflow due to differential restrictor
6746 | Differential term abnormal
6747 | PID result abnormal
6748-6759 | Reserved
6760-6799 High-speed input/output error code | 
6760 | Number of high-speed input instruction running entries exceeding limit
6761 | High-speed input C counter multiplexing error
6762 | High-speed input instruction port repeated or conflict

## Slide 57
Diagnostics
PART 4
Error Code | Content
D8067 | Instruction parameter & running parameter incorrect
6763 | High-speed input instruction element exceeding range
6764 | High-speed input instruction data exceeding range
6765 | High-speed output instruction element exceeding range
6766 | High-speed output instruction data exceeding range
6767 | Conflict in comparison objects setting of high-speed interruption comparison instruction
6768 | Reserved
6769 | Reserved
6770 | High-speed output instruction port repeated or conflict
6771 | High-speed output instruction signal incorrect
6772 | Motion control subroutine program instruction incorrect, compiling incorrect or not existing
6773 | Motion control subroutine program invoking error
6774 | Reserved
6775 | Motion control subroutine program instruction element exceeding range, function word not matching or existing
6776 | Motion control subroutine program data incorrect or exceeding range
6777 | High-speed interpolation instruction arc length too small
6778 | High-speed interpolation instruction arc parameter incorrect (center or circle setting incorrect, radius too long), resulting in arc generating failure
6779 | Helical curve 3rd axis pulses of high-speed output interpolation instruction exceeding range
6780-6799 | Reserved
16700-16799 | Reserved
26700-26799 | Reserved

## Slide 58
Forward, Always Progressing !